SECTION 07 21 13.5

CONTINUOUS INSULATION XCI 286 WALL/CEILING PANELS

This specification is based on the continuous insulation products of Hunter Panels, located at:

15 Franklin Street

Portland, Maine 04101

Phone: (207) 761-5678

Toll Free: (888) 746-1114

Fax: (877) 775-1769

E-mail: info@hpanels.com

Internet: www.hunterpanels.com

Hunter Panels has been an industry leader in Polyiso insulation for over 20 years. Hunter’s Xci products are designed for use in commercial and residential wall applications to provide “ci” continuous insulation and weather resistive barrier performance within the building envelope.

This specification includes Xci 286, an energy efficient rigid insulation panel composed of a closed cell Class A polyisocyanurate foam core bonded on-line during a restrained-rise manufacturing process to 15-mil thick glass fiber-reinforced foil facers, one side reflective, one side with a white acrylic coating. Xci 286 is designed for use as interior or exterior continuous insulation in a wall assembly capable of meeting NFPA 285 and for exposed interior wall or ceiling use meeting NFPA 286 acceptance criteria. Typical commercial and residential applications include industrial buildings, warehouses, pre-engineered metal buildings, agricultural buildings, basements/attics/crawlspaces, parking garages, and concrete and masonry wall applications. For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based on NFPA 285 Tests on our website, www.hunterpanels.com.  With proper seam treatment, Xci 286 can be used a complete weather barrier.

Follow the instructions listed in the **NOTE TO SPECIFIER** sections included throughout the specification. Edit carefully to suit project requirements. Modify as necessary and delete paragraphs that are not applicable.

GENERAL

SECTION INCLUDES

SPECIFIER INSTRUCTIONS -  Delete any paragraphs below not applicable to project.

Xci 286 Continuous Exposed Interior Wall or Ceiling Insulation Panels

Xci 286 Continuous Insulation for Exterior Walls

** NOTE TO SPECIFIER ** - Delete any paragraphs below not applicable to project.

RELATED SECTIONS

SPECIFIER INSTRUCTIONS -  Delete sections below not relevant to this project; add others as required.

Section 03 30 00 - Cast In Place Concrete: Concrete base wall.

Section 03 40 00 - Pre-Cast Concrete: Pre-cast concrete base wall.

Section 04 21 00 - Clay Masonry: Brick facing.

Section 04 22 00 - Concrete Unit Masonry: Masonry base wall.

Section 04 40 00 - Stone Facing.

Section 05 40 00 - Cold Formed Metal Framing.

Section 07 26 00 - Vapor Retarders: Vapor retarder materials over insulation to adjacent insulation.

Section 07 27 00 - Air Barriers: Air seal materials over insulation to adjacent insulation.

Section 09 20 00 - Plaster and Gypsum Board.

Section 09 22 16 - Non-Structural Metal Framing.

Section 09 24 23 - Stucco.

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section; add others as required.

REFERENCES

SPECIFIER INSTRUCTIONS -  Delete references from the list below that are not actually required by the text of the edited section; add others as required.

ASTM C 209 – Methods of Testing Insulating Board, Structural and Decorative.

ASTM C 518 – Steady State Thermal Transmission by Means of the Heat Flow Meter Apparatus (R Value)

ASTM C 1289 – Specifications for Faced Rigid Cellular Polyisocyanurate Thermal Insulating Board.

ASTM D 1037 - Standard Test Methods for Evaluating Properties of Wood-Base Fiber and Particle Panel Materials.

ASTM D 1621 – Test Methods for Compressive Properties of Rigid Cellular Plastics.

ASTM D 2126 - Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging.

ASTM D 3273 - Standard Test Method for Resistance to Growth of Mold on the Surface of Interior Coatings in an Environmental Chamber.

ASTM E 84 (UL 723)  - Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E 96 - Test Method for Water Vapor Transmission of Materials.

ASTM E 283 – Standard Test Method for Determining Rate of Air Leakage through Exterior Window, Curtain Walls and Doors under specific Pressure differences across the specimen

ASTM E 330 – Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference.

ASTM E 331 – Standard Test Method for Water Penetration of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference

ASTM E 2178 – Standard Test Method for Air Permeance of Building Materials

ASTM E 2357 – Standard Test Method for Determining Air Leakage of Air Barrier Assemblies

ASHRAE 90.1 - Energy Standard for Buildings Except Low-Rise Residential Buildings.

IBC Chapter 26 – Foam Plastic Insulation.

NFPA 285 - Standard Fire Test Method For Evaluation Of Fire Propagation Characteristics Of Exterior Non-Load-Bearing Wall Assemblies Containing Combustible Components.

NFPA 286 - Standard Methods Of Fire Tests For Evaluating Contribution Of Wall And Ceiling Interior Finish To Room Fire Growth

UL 1715 - Standard for Fire Test of Interior Finish Material.

UL 263 – Standard for Fire Tests of Building Construction and Materials

California Code of Regulations, Title 24, Insulation Quality Standard License #TI-1420

CCMC 13460-L

CAN/ULC S-704 Type 1, Class 1

X.	DrJ Engineering TER 1402-01: Fire Performance; Air and Water-Resistive Barrier Performance

Y.	Priest and Associates Engineering Extensions Based on NFPA 285 Tests

SPECIFIER INSTRUCTIONS - Edit the System Descriptions to include those applicable to the project requirements.

XCI 286 is capable of meeting both NFPA 285 and NFPA 286. NFPA 286 for exposed interior wall or ceiling use in commercial, residential, industrial, agricultural and metal building applications; and for approved assemblies meeting NFPA 285 for Base Wall Systems of Concrete Masonry, Concrete, and Steel Studs together with approved exterior assemblies and facings for each.

Continuous XCI 286 insulation wall panels are intended to be used as exposed interior and non-exposed exterior continuous insulation over framing members and to be relatively free of significant thermal bridging. Coordinate with other trades to minimize the penetration of thermal conductors through the wall system. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is a critical element of a continuous insulation wall assembly. It is strongly recommended that the Architect perform a hygrothermal analysis of the assembly at the location of each project using local code requirements and ASHRAE Standards. The calculations should be used to verify the performance of the assembly and to determine the locations of the weather resistant barrier(s) as required.

SPECIFIER INSTRUCTIONS - Include the following paragraph for XCI 286 insulation used in exposed interior walls or ceilings without the need for a covering system.

** NOTE TO SPECIFIER ** - Delete sections below not relevant to this project; add others as required

SPECIFIER INSTRUCTIONS - The following three paragraphs include approved assemblies meeting NFPA 285 for Base Wall Systems of Concrete Masonry, Concrete, and Steel Studs together with approved exterior assemblies and facings for each. Select the Base Wall System and Exterior Finish for each and delete those not applicable. NFPA test results for the systems specified are not available in the UL directory. They are only available after passing large scale tests in accordance with NFPA 285. Contact Hunter for additional information on approved assemblies.

DESIGN REQUIREMENTS

    - Perform work in accordance with all federal, state and local codes.

Physical properties of Xci 286 (faced):

Flame Spread Index: ASTM E 84, less than 25.

Smoke Developed: ASTM E 84, less than 250.

Compressive Strength: ASTM D 1621; Grade 2 (20psi / 138 kPa) or Grade 3 (25psi / 172 kPa).

Dimensional Stability: ASTM D 2126, 2 percent linear change (7 days).

Moisture Vapor Permeance: ASTM E 96, less than 0.04 perm (2.875ng/(Pa•s•m2)).

Water Absorption: ASTM C 209, less than 0.05 percent by volume.

Service Temperature: Minus 100 degrees to 250 degrees F (Minus 73 degrees C to 122 degrees C).

Air Permeance of Building Material: ASTM E 2178, less than 0.001 L(s.m2) at 75 Pa

Air Leakage of Air Barrier Assemblies: ASTM E 2357, no leakage

Rate of Air Leakage: ASTM E 283, less than 0.04 cfm/ft2

Structural Performance by Uniform Static Air Pressure Difference: ASTM E 330, less than 0.04 cfm/ft2

Water Penetration by Static Air Pressure Difference: ASTM E 331, pass, no leakage

Resistance to Mold: ASTM D 3273 Passed (10).

Impact Resistance: ASTM D1037 (Janka Ball Test): 40

Pressure washable 15 mil reinforced foil facer

3rd Generation Zero ODP Blowing Agent; Contains zero CFCs, HCFCs, or HFCs; Virtually no Global Warming Potential (GWP)

Hunter Xci 286 has passed the following:

Meets the current continuous insulation standards of ASHRAE 90.1, IECC, and IBC Chapter 26.

NFPA 286 Corner Burn Test for walls or ceilings only, with or without joint treatment, allowing product to be left exposed on interior application without a thermal barrier up to 3.5 inches thick.

UL 1715 with up to 8 inches for exposed applications on ceilings only. Can be installed in multiple layers as needed.

NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components. For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based On NFPA 285 Test on our website, www.hunterpanels.com.

UL 263 Time Rated Assemblies

D.      Hunter Panels Xci 286 is evaluated and listed under DRJ TER 1402-01. Tests include:

1.        Flame spread index of <25 and smoke developed index of <250 when tested in accordance with ASTM E 84.

2.       Classified as Type I in accordance with ASTM C 1289.

3.       Air Barrier Performance per ASTM E 2178

** NOTE TO SPECIFIER ** - Delete paragraphs that are not applicable.

SUBMITTALS

Submit under provisions of Section 01 33 00.

Product Data:  Manufacturer's data sheets and installation guides on wall panels and fasteners to be used, including:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods and accessories.

SPECIFIER INSTRUCTIONS -  Delete the following paragraphs if LEED is not applicable.

LEED Submittals:  Provide documentation of how the requirements of Credit will be met:

List of proposed materials with recycled content.  Indicate post-consumer recycled content and pre-consumer recycled content for each product having recycled content.

Manufacturer-Specific Environmental Product Declaration (EPD) which conforms to ISO 14025 and Polyisocyanurate Insulation Manufacturers Association EPD

D.	DrJ Engineering TER 1402-01 (state-specific stamped reports available)

E.	Priest and Associates Engineering Extensions Based on NFPA 285 Tests

F.       Manufacturer's Certificate:  Certify panels will conform to specified performance   requirements.

QUALITY ASSURANCE

Manufacturer Qualifications: Manufacturer shall be a company that regularly manufactures and assembles specified insulation in house with no outside fabrication operations.

Manufacturer shall have multiple manufacturing facilities to ensure consistency of product supply.

Pre-Installation Meeting:  Convene minimum one week prior to commencing Work of this section. Review installation procedures and coordination required with Related Work and  include the following:

Participants: Authorized representatives of the Contractor, Architect, Installer, and Manufacturer.

Review wall assemblies for potential interference and conflicts and coordinate layout and support provisions for interfacing work.

Review continuous insulation wall panels installation methods and procedures related to application, including manufacturer’s installation guidelines.

Review firestopping requirements and weather resistive membrane requirements and placement locations.

Review field quality control procedures.

DELIVERY, STORAGE, AND HANDLING

A.	Good construction practice dictates that all insulations should be protected from moisture and direct sunlight during job-site storage. Pallets of Hunter Panels Xci 286 are protected by a 2-step packaging process using shrink wrap and a UV resistant polyethylene bag. This moisture resistant package is designed for protection from the elements during flatbed shipment from our factories to the job-site.  Outdoor storage for extended periods of time requires waterproof tarpaulins and elevated storage above ground level a minimum of 2”.  Additionally, we recommend slitting the bundle packaging vertically down the center of the two short sides to prevent moisture accumulation within the package.

B.	Protect insulation from open flame.

SEQUENCING

Coordinate with the installation of vapor retarders and air seal materials specified is Section 07 26 00 and Section 07 27 00.

Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

PRODUCTS

MANUFACTURERS

Basis of Design: Xci 286 produced by Hunter Panels, 15 Franklin Street, Portland, Maine 04101. Phone: (207) 761-5678 or (888) 746-1114. Fax: (717) 960-1611. Email: info@hpanels.com.  Website: www.hunterpanels.com

** NOTE TO SPECIFIER ** - Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

SPECIFIER INSTRUCTIONS -  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions:  Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01600.

BOARD INSULATION

Hunter Panels Xci 286 complies with ASTM C 1289 (Type I) and ASTM E 84 Class A. Boards are energy efficient rigid insulation panels composed of a closed cell Class A polyisocyanurate foam core bonded during a restrained-rise manufacturing process to 15-mil thick reinforced foil facers, one side reflective, one side with a white acrylic coating. Type II per ASTM C1289

Foam Core:

a.	Grade 2 (20 psi)_

b.	Grade 3 (25 psi)

2.       Panel Size:

4 feet by 8 feet (1220 mm by 2440 mm).

Additional lengths/widths available upon request

3.       Thickness / R Value: ASTM C 518 at 75 degrees F (23.9 degrees C).

SPECIFIER INSTRUCTIONS -  Select one of the following Grade paragraphs and delete those not required.

1.0 inches (25 mm) / R Value 6.3

1.5 inches (38 mm) / R Value 9.5

1.6 inches (41 mm) / R Value 10.1

2.0 inches (51 mm) / R Value 13.0

2.5 inches (64 mm) / R Value 16.0

3.0 inches (76 mm) / R Value 19.0

3.5 inches (89 mm) / R Value 22.0

4.0 inches (100 mm) / R Value 25.2

4.       Provide to the thickness indicated on the Drawings.

** NOTE TO SPECIFIER **  Sealing the joints is an option but is not required by Hunter XCI.  If required, select one of the following paragraphs for panel joint sealing and panel fastening using foil face or white face as determined by product placement. Delete those not required. Designers who wish to use the face of the boards as a vapor barrier by sealing the seams or by applying fluid WRBs are responsible for performing a hygrothermal analysis of the assembly using local code requirements and ASHRAE Standards.

  - JOINT SEALANT, PANEL FASTENERS, AND ADHESIVES

Liquid Sealants:

Xci BarriBond XL

Xci BarriBond

Xci DynaTrol I-XL Hybrid

Xci Foil Grip 1402: Foil-faced butyl flashing tape

Backing: 2 mils Aluminum foil.

Width: 2 to 6 inches.

Thickness: 17 mils.

Xci Aluma Grip 701: Foil-faced butyl flashing tape

a.	Backing: 2 mils Aluminum foil.

b.        Width: 2 to 6 inches.

c.        Thickness: 30 mils.

4.	ECHOtape MT-A7757: Foil-faced acrylic flashing tape.

a.	Width: Nominal 2.0”, 3.0”, and 4.0”

b.       Thickness: 3.35 mils

5.       Venture Tape 1558 HT by 3M- White acrylic tape

6.       Construction Adhesives: Loctite, Chemlink, DAP, BASF

7.       Insulation Adhesive: CAV-GRIP

8.       Approved Fastening Methods:

SPECIFIER INSTRUCTIONS -  Select one of the following fastener paragraphs and delete those not required.

Screw type with washers: TRUFAST Walls

Powder or gas actuated fasteners with washers

Impalement type: Stick pins

Adhesive; any general construction grade adhesive

Insulation retainment systems for exposed applications: Victory Bear or Nudo Products

EXECUTION

** NOTE TO SPECIFIER **** NOTE TO SPECIFIER ** - See Hunter Panel Installation Guide for recommended fastening patterns and installation methods. Coordinate panel installation requirements with wall covering manufacturer

SPECIFIER INSTRUCTIONS -  See Hunter Panel Installation Guide for recommended fastening patterns and installation methods. Coordinate panel installation requirements with wall covering manufacturer.

EXAMINATION

Do not begin installation until exterior walls have been properly prepared.

Verify that all exterior wall assembly construction has been completed to the point where the insulation may correctly be installed.

Verify that mechanical and electrical services in walls have been installed and tested and, if appropriate, verify that adjacent materials and finishes are dry and ready to receive insulation.

If wall assembly preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

PREPARATION

Clean surfaces thoroughly prior to installation as needed..

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install in accordance with manufacturer's instructions.

SPECIFIER INSTRUCTIONS - Select one of the following two paragraphs and delete the one not required.

Install with white or reflective side exposed.

Install without gaps or voids. Do not compress insulation.

Trim insulation neatly to fit spaces. Insulate miscellaneous gaps and voids.

Fit insulation tight in spaces and tight to exterior side of mechanical and electrical services within plane of insulation.

Fasten or adhere insulation as recommended by the manufacturer’s Installation Guide.

Insulation must be protected from open flame and stored in accordance with the manufacturer’s instructions.

SPECIFIER INSTRUCTIONS -  During the time between installation of continuous wall insulation panels and the application of the finished exterior cladding, it is recommended that a building wrap be applied over the wall insulation. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is also a critical element of the wall assembly. It is recommended that a hygrothermal analysis of the proposed assembly be conducted to determine the type and locations of a proposed Weather Resistant Barriers. Select one of the following three paragraphs and delete those not required.

Install vapor retarders over insulation panels as specified in Section 07260.

Install air barriers over insulation panels as specified in Section 07270.

Hunter Xci wall insulation is not intended to be left exposed for extended periods of time without adequate protection. If extended exposure is anticipated all exposed foam surfaces including corners, window and door openings, should be taped with a compatible waterproof tape.  With proper installation, Xci 286 can be left exposed for up to 180 days.

Install exterior cladding as recommended by the cladding manufacturer and as specified in other sections of this specification.

PROTECTION

Protect installed products until completion of project.

Cover the top and edges of unfinished wall panel work to protect it from the weather and to prevent accumulation of water in the cores of the panels.

Wet panels shall be allowed to completely dry prior to application of vapor barrier and/or cladding.

Repair or replace damaged products before Substantial Completion.

END OF SECTION