SECTION 07 21 13

CONTINUOUS INSULATION XCI CG WALL PANELS

This specification is based on the exterior continuous insulation products of Hunter Panels, located at:

15 Franklin Street

Portland, Maine 04101

Phone: (207) 761-5678

Toll Free: (888) 746-1114

Fax: (877) 775-1769

E-mail: info@hpanels.com

Internet: www.hunterpanels.com

Hunter Panels has been an industry leader in Polyiso insulation for over 20 years. Hunter’s Xci products are designed for use in commercial and residential wall applications to provide “ci” continuous insulation and air barrier performance within the building envelope.

This specification includes Xci CG, an energy efficient rigid insulation panel composed of a closed cell polyisocyanurate foam core bonded online during a restrained-rise manufacturing process to premium performance polymer bonded glass mat facers on both sides.  Xci CG can be applied to the interior or exterior of structural exterior walls and can be used in wall assemblies meeting the acceptance criteria of NPFA 285.   For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based on NFPA 285 Tests on our website, www.hunterpanels.com.  With proper seam treatment, Xci CG can be used as an air barrier in the wall assembly.

Follow the instructions listed in the ** NOTE TO SPECIFIER ** sections included throughout the specification. Edit carefully to suit project requirements. Modify as necessary and delete paragraphs that are not applicable.

GENERAL

SECTION INCLUDES

** NOTE TO SPECIFIER **  Delete any paragraphs below not applicable to project.

Xci CG Continuous Insulation for Exterior Walls

** NOTE TO SPECIFIER ** - Delete any paragraphs below not applicable to project.

RELATED SECTIONS

Section 03300 - Cast In Place Concrete: Concrete base wall.

Section 03400 - Pre-Cast Concrete: Pre-cast concrete base wall.

Section 04210 - Clay Masonry: Brick facing.

Section 04800 - Masonry Assemblies: Masonry base wall.

Section 04850 - Stone Facing.

Section 05400 - Cold Formed Metal Framing.

Section 07260 - Vapor Retarders: Vapor retarder materials over insulation to adjacent insulation.

Section 07270 - Air Barriers: Air seal materials over insulation to adjacent insulation.

Section 09110 - Non-Structural Metal Framing.

Section 09200 - Plaster and Gypsum Board.

Section 09220 - Stucco.

REFERENCES

** NOTE TO SPECIFIER **  Delete references from the list below that are not actually required by the text of the edited section; add others as required.

ASTM C 209 – Methods of Testing Insulating Board, Structural and Decorative.

ASTM C 518 – Steady State Thermal Transmission By Means Of The Heat Flow Meter Apparatus (R Value).

ASTM C 1289 – Specifications for Faced Rigid Cellular Polyisocyanurate Thermal Insulating Board.

ASTM D 1037 - Standard Test Methods for Evaluating Properties of Wood-Base Fiber and Particle Panel Materials.

ASTM D 1621 – Test Methods for Compressive Properties of Rigid Cellular Plastics.

ASTM D 2126 - Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging.

ASTM D 3273 - Standard Test Method for Resistance to Growth of Mold on the Surface of Interior Coatings in an Environmental Chamber.

ASTM E 84 – Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E 96 - Test Method for Water Vapor Transmission of Materials.

ASTM E 2178 – Standard Method for Air Permeance of Building Materials.

NFPA 285 - Standard Fire Test Method For Evaluation Of Fire Propagation Characteristics Of Exterior Non-Load-Bearing Wall Assemblies Containing Combustible Components.

L.	Priest and Associates Engineering Extensions Based on NFPA 285 Tests

M.	DrJ Engineering TER 1402-02

N.	ASHRAE 90.1- Energy Standard for Buildings Except Low-Rise Residential Buildings

O.	IBC Chapter 26- Foam Plastic

P.	UL 263- Standard for Fire Tests of Building Construction and Materials

Q.	Miami Dade Product Control – Notice of Acceptance NOA No. 14-0501.01

R.	California Code of Regulations, Title 24, Insulation Quality Standard License #TI-1420

S.	CAN/ULC S-704 Type 2, Class 2

T.	CCMC 13460-L

** NOTE TO SPECIFIER ** System Description contains components which must be part of an NFPA 285 compliant assembly.  Hunter Panels has an Engineering Extension Report from Priest & Associates that outlines all compliant wall assembly options for Types I, II, III and IV buildings that can be achieved using Xci CG. For a complete list of NFPA 285 compliant assembly options please contact our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based on NFPA 285 Tests on our website, www.hunterpanels.com.

** NOTE TO SPECIFIER **  Continuous insulation wall panels are intended to be used continuous over framing members and to be relatively free of significant thermal bridging. Coordinate with other trades to minimize the penetration of thermal conductors through the wall system. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is a critical element of a continuous insulation wall assembly. It is strongly recommended that the Architect perform hygrothermal analysis of the assembly at the location of each project using local code requirements and ASHRAE Standards. The calculations should be used to verify the performance of the assembly and to determine the locations of the weather resistant barrier(s) as required.

SYSTEM DESCRIPTION

A.	Exterior Wall Assembly; Exterior Insulation (Table 1 of Engineering Extension Report)

1.	Base Wall

2.	Fire-stopping at floor lines

3.	Cavity Insulation (optional)

4.	Exterior Sheathing, Sheathing/WRB combined product (optional)

5.	WRB on base wall (optional)

6.	Exterior Insulation

7.	WRB on Exterior Insulation (optional)

8.	Exterior Cladding

B.	Exterior Wall Assembly; Interior Insulation (Table 6 of Engineering Extension Report)

1.	Base Wall

2.	Exterior Coating (optional)

3.	WRB over Base Wall Interior (optional)

4.	Continuous Insulation

5.	WRB over Continuous Insulation (optional)

6.	Interior Cladding

** NOTE TO SPECIFIER ** - Delete sections below not relevant to this project; add others as required.

** NOTE TO SPECIFIER ** The following four paragraphs contain various IBC non-combustible wall types for Types I, II, III and IV Construction with minimum requirements to meet NFPA 285 requirements. NFPA test results are not available in the UL directory. They are only available after passing large scale tests in accordance with NFPA 285. Select the approved assemblies meeting NFPA 285 for Base Wall Systems of Concrete Masonry, Concrete, Steel Studs and Fire Treated Wood Studs together with approved exterior assemblies for each as required from the following paragraphs and delete those not required. Coordinate the Drawings with the following applications paragraphs. Contact Hunter for additional information on approved assemblies.

DESIGN REQUIREMENTS

    - Perform work in accordance with all federal, state and local codes.

Physical properties (Foam Core):

Water Absorption: ASTM C 209, less than 0.1 percent by volume

Impact Resistance: ASTM D 1037 (Janka Ball Test): 15

Compressive Strength: ASTM D 1621; Type II, Grade 2 (20 psi/138 kPa) and Grade 3 (25 psi/172 kPa)

Dimensional Stability: ASTM D 2126, 2 percent linear change (7 days)

Moisture Vapor Permeance: ASTM E 96, less than 1 perm (57.5ng/(Pa*s*m2)

Air Permeance of Building Material: ASTM E 2178, less than 0.001 L(s*m2) at 75 Pa

Resistance to Mold: ASTM D 3273 Passed (10)

Service Temperature: Minus 100 degrees F to 250 degrees F (Minus 73 degrees C to 122 degrees C)

3rd Generation Zero ODP Blowing Agent; Contains zero CFCs, HCFCs, or HFCs; Virtually zero Global Warming Potential (GWP)

C.       Hunter Xci CG has passed the following:

1.       Meets the current continuous insulation standards of ASHRAE 90.1, IECC and IBC Chapter 26.

2.        NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components. For a complete list of NFPA 285 compliant assembly options please call our technical team at 888-746-1114 or reference the report titled Engineering Extensions Based On NFPA 285 Test on our website, www.hunterpanels.com.

3.	UL 263 Time-Rated Assemblies

D.       Hunter Panels Xci CG is evaluated and listed under DrJ TER 1402-02. Tests include:

1.       Flame spread index of <75 and smoke developed index of <450 when tested in accordance with ASTM E 84.

2.      Classified as Type II, Class 2 in accordance with ASTM C 1289.

3.	Air Barrier Performance per ASTM E 2178

SUBMITTALS

Submit under provisions of Section 01300.

Product Data:  Manufacturer's data sheets and installation guides on wall panels including:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods and accessories.

** NOTE TO SPECIFIER ** - Delete the following paragraphs if LEED is not applicable.

C.       LEED Submittals:  Provide documentation of how the requirements of Credit will be met:

1.       List of proposed materials with recycled content.  Indicate post-consumer recycled content and pre-consumer recycled content for each product having recycled content.

2.      Manufacturer-Specific Environmental Product Declaration (EPD) which conforms to ISO 14025 and Polyisocyanurate Insulation Manufacturers Association EPD

D.	DrJ Engineering TER 1402-02 (state-specific stamped reports available)

E.	Priest and Associates Engineering Extensions Based on NFPA 285 Tests

F.       Manufacturer's Certificate:  Certify panels will conform to specified performance   requirements.

** NOTE TO SPECIFIER **  Delete the following paragraphs if LEED is not applicable.

QUALITY ASSURANCE

A.	Manufacturer shall be a company that regularly manufactures and assembles specified insulation in house with no outside fabrication operations.

B.	Manufacturer shall have multiple manufacturing facilities to ensure consistency of product supply.

C.	Pre-Installation Meeting: Convene minimum one week prior to commencing Work of this section. Review installation procedures and coordination required with Related Work and include the following:

1.       Participants: Authorized representatives of the Contractor, Architect, Installer, and Manufacturer.

2.       Review wall assemblies for potential interference and conflicts and coordinate layout and support provisions for interfacing work.

3.       Review continuous insulation wall panels installation methods and procedures related to application, including manufacturer’s installation guidelines.

4.       Review firestopping requirements and weather resistive membrane requirements and placement locations.

5.      Review field quality control procedures.

DELIVERY, STORAGE, AND HANDLING

A.	Good construction practice dictates that all insulations should be protected from moisture and direct sunlight during job-site storage. Pallets of Hunter Panels Xci CG are protected by a 2-step packaging process using shrink wrap and a UV resistant polyethylene bag. This moisture resistant package is designed for protection from the elements during flatbed shipment from our factories to the job-site.  Outdoor storage for extended periods of time requires waterproof tarpaulins and elevated storage above ground level a minimum of 2”.  Additionally, we recommend slitting the bundle packaging vertically down the center of the two short sides to prevent moisture accumulation within the package.

SEQUENCING

Coordinate with the installation of vapor retarders and air seal materials specified is Section 07260 and Section 07270.

Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

PRODUCTS

MANUFACTURERS

Basis of Design: Xci CG produced by Hunter Panels, 15 Franklin Street, Portland, Maine 04101. Phone: (207) 761-5678 or (888) 746-1114. Fax: (877) 775-1769. E-mail: info@hpanels.com.

** NOTE TO SPECIFIER ** - Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions

** NOTE TO SPECIFIER **  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions:  Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01600.

BOARD INSULATION

Hunter Panels Xci CG complies with ASTM C1289 Type II, Class 2 and ASTM E84 Class B.  Boards are energy efficient rigid insulation panels composed of a closed cell polyisocyanurate foam core bonded online during a restrained-rise manufacturing process to premium performance polymer bonded glass mat facers on both sides.

B.	1.	Foam Core

a.	Grade 2 (20psi)

b.	Grade 3 (25psi)

2.	Panel Size:

a.	4 feet by 8 feet (1220 mm by 2440 mm)

b.	Additional lengths/widths available upon request

3.	Thickness / R Value: ASTM C 518 at 75 degrees F (23.9 degrees C).

** NOTE TO SPECIFIER **  Select one of the following Grade paragraphs and delete those not required. Values calculated based on 5/8 inch plywood facing.

1.0 inches (25 mm) / R Value 6.0

1.5 inches (38 mm) / R Value 9.0

2.0 inches (51 mm) / R Value 12.1

2.5 inches (64 mm) / R Value 15.3

3.0 inches (76 mm) / R Value 18.5

3.3 inches (84 mm) / R Value 20.4

3.5 inches (89 mm) / R Value 21.7

4.0 inches (102 mm) / R Value 25.0

Provide to the thickness indicated on the Drawings.

** NOTE TO SPECIFIER **  Several factors are involved in the proper fastening of insulation panels. These include overall thickness of the panel, the weight of the specified cladding and the type of support provided at the base of the wall assembly. Please contact Hunter Panels for assistance with fastening rate and fastener type.

JOINT SEALANT, PANEL FASTENERS, AND ADHESIVES

1.	Liquid Joint Sealants:

a.	Xci BarriBond XL

b.	Xci BarriBond

c.	Xci DynaTrol I-XL Hybrid

2.	Foil Grip 1402 Tape: Foil-faced butyl flashing tape

a.	Backing: 2 mils aluminum foil

b.	Width: 2 to 6 inches

c.	Thickness: 17 mils

3.	AlumaGrip 701 Tape: Foil-faced butyl flashing tape

a.	Backing: 2 mils aluminum foil

b.	Width: 2 to 6 inches

c. 	Thickness: 30 mils

4.	ECHOtape MT-A7757: Foil-faced acrylic flashing tape.

a.	Width: Nominal 2.0”, 3.0”, and 4.0”

b.	Thickness: 3.35 mils

5.	Construction Grade Adhesives including: Loctite, Chemlink, DAP, BASF

6.	Insulation Adhesive: CAV-GRIP

7.	Approved Fastening Methods:

a.	Screw type with washers (TRUFAST Walls)

b.	Powder or gas-actuated fasteners with washers

c.	Impalement type (stick pins)

d. 	Adhesive: any general construction grade adhesive (not recommended for ceiling applications)

EXECUTION

** NOTE TO SPECIFIER **** NOTE TO SPECIFIER ** - See Hunter Panel Installation Guide for recommended fastening and installation methods. Coordinate panel installation requirements with wall covering manufacturer

** NOTE TO SPECIFIER **  See Hunter Panel Installation Guide for recommended fastening patterns and installation methods. Coordinate panel installation requirements with wall covering manufacturer.

EXAMINATION

Do not begin installation until exterior walls have been properly prepared.

Verify that all exterior wall assembly construction has been completed to the point where the insulation may correctly be installed.

Verify that mechanical and electrical services in walls have been installed and tested and, if appropriate, verify that adjacent materials and finishes are dry and ready to receive insulation.

If wall assembly preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

PREPARATION

Clean surfaces thoroughly prior to installation.

Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

INSTALLATION

Install in accordance with manufacturer's instructions.

Install in exterior spaces without gaps or voids. Do not compress insulation.

Trim insulation neatly to fit spaces. Insulate miscellaneous gaps and voids.

Fit insulation tight in spaces and tight to exterior side of mechanical and electrical services within plane of insulation.

Fasten insulation as recommended by the Hunter Panel Installation Guide. Provide base support for the insulation panels as required for the exterior cladding to be installed over the panels.

Insulation must be protected from open flame and stored in accordance with the manufacturer’s instructions.

** NOTE TO SPECIFIER **  During the time between installation of continuous wall insulation panels and the application of the finished exterior cladding, it is recommended that a building wrap be applied over the wall insulation. The incorporation of Weather Resistant Barriers (air, vapor and moisture) is also a critical element of the wall assembly. It is recommended that a hygothermal analysis of the proposed assembly be conducted to determine the type and locations of a proposed Weather Resistant Barriers. Select one of the following three paragraphs and delete those not required.

Install vapor retarders over insulation panels as specified in Section 07260.

Install air barriers over insulation panels as specified in Section 07270.

Hunter Xci wall insulation is not intended to be left exposed for extended periods of time without adequate protection. If extended exposure is anticipated all exposed foam surfaces exposed to daylight should be taped with a compatible waterproof tape.

Install exterior cladding as recommended by the cladding manufacturer and as specified in other sections of this specification.

PROTECTION

Protect installed products until completion of project.

Cover the top and edges of unfinished roof panel work to protect it from the weather and to prevent accumulation of water in the cores of the panels.

Do not leave panels exposed to moisture. Wet panels shall be removed or allowed to completely dry prior to application of vapor barrier and/or roof covering.

Repair or replace damaged products before Substantial Completion.

END OF SECTION